MINI DC Series

30KW 40KW 60KW Wall Mount DC Fast Charger

User Manual & Installation  Instructions

30KW

40KW

60KW

CONTENT

Introductions	1

Features		1

Applications	1

1. Basic User Interface	2

1.Basic User Interface	3

1.Basic User Interface	4

2. Specification	5

2.1 Product Specification	5

2.2 Dimmensions (Unit: mm)	6

3. Installation Instruction	9

3.1 Before Installation	9

3.2 Grounding and Safety Requirement	10

3.3 Service Wiring	11

3.4 Unpack the charger	12

3.5 Recommended Tools for Installation and Inspection	14

3.6 Installation Procedure	15

3.7 Installation Inspection & Commissioning	20

4. Network Setting	23

4.1 Wi-Fi Network Setting	23

5. Operation Process	25

5.1 RGB LED indicators	25

5.2 LCD indicators	25

5.3 Troubleshooting	29

5.4 Status Codes	30

6. Maintenance	31

6.1 General Maintenance	31

Limited Product Warranty	32

Appendix - Package list	33

Introductions

The Wall Mount DC Fast Charger is the top choice to power battery electric vehicles (BEV) and plug-in electric vehicles (PHEV). It is designed for quick charging in both public and private locations, such as retail and commercial parking spaces, fleet charging stations, highway service areas, workplace, residence, etc.

The Wall Mount DC Fast Charger has the advantage of easy installation. The wall-mounted design and pluggable power modules realize flexible and cost-effec- tive installation for different types of locations. The DC Wall-Mounted charger also has network communication capability. It is able to connect with remote network systems and provide drivers of electric cars real-time information, such as the location of charging stations, charging progress and billing information. The Wall Mount DC Fast Charger has a clear user interface with function buttons, safety cer- tiﬁcations and an excellent waterproof and dust proof design to provide the best choice for outdoor environments.

Features

- Wall-Mounted design and pluggable power modules make installation easy and flexible.

- Offers customers the convenience of start/stop charging control from an autho- rized RFID smart card or mobile APP.

- Built on latest industry standards for DC charging.

- Carries an outdoor rating capable of withstanding solid and liquid intrusions in outdoor settings making the unit more stable and highly reliable.

- Provides a high-contrast, screen interface with multi-function buttons.

Applications

- Public and private parking areas

- Community parking areas

- Parking areas of hotels, supermarkets and shopping malls

- Workplace parking areas

- Charging stations

- Highway rest areas

- Basic User Interface

Main unit   30KW

1.Basic User Interface

Main unit      40KW

1.Basic User Interface

Main unit      60KW

- Specification

  - Product Specification

| Model | QTEV30K-D3M | QTEV40K-D4M | QTEV60K-D5M |
| --- | --- | --- | --- |
| Technical features |  |  |  |
| Max Power | Up to 30KW | Up to 40KW | Up to 60KW |
| Input/Output power | 400VAC±10%-50/60Hz-3phase | 400VAC±10%-50/60Hz-3phase | 400VAC±10%-50/60Hz-3phase |
| Power factor | 0.98 |  |  |
| Efficiency | >95% |  |  |
| Measuring accuracy | Level 0.5 |  |  |
| Output voltage range | CCS: 300~1000VDC |  |  |
| Output current range | 0-100A | 0-100A*2 | 0-200A*2 |
| Communication | Ethernet/WIFI/4G/OCPP 1.6 Json (OCPP 2.0 optional) |  |  |
| User interface | RFID card and APP |  |  |
| Display | LCD 7 inch Touch Screen |  |  |
| Versatility | IEC61851/IEC62196/ISO1511/DIN70121/EN61000-6-4:2007 |  |  |
| Energy Meter | CE certified |  |  |
| RCD | Type A or Type B(optional) |  |  |
| Security design | Over/under voltage protection, overload protection, current leakage protection, grounding protection,lightening surge protection |  |  |
| DC Plugs | CCS2 Cable 5M | CCS2*2 Cable 5M | CCS2*2 Cable 5M |
| Physical properties |  |  |  |
| Warranty | 2 years |  |  |
| Application place | Indoor/Outdoor |  |  |
| Installation method | Wall mount, pedestal mount (optional) |  |  |
| Sound noise | <55DB in all directions |  |  |
| Operating temperature | -20℃ to +50℃ |  |  |
| Humidity | Max.95%(non-regulating) |  |  |
| Dimensions | 670*460*270mm | 770*560*206mm | 900*650*260mm |
| Package Dimension | 800*590*480mm | 1010*720*510mm | 1200*920*450mm |
| Net Weight | 41Kg | 75Kg | 115Kg |
| Gross Weight | 46Kg | 78Kg | 120Kg |

  - Dimmensions (Unit: mm)

Main Size of Charger:30KW

Dimmensions (Unit: mm)

Main Size of Charger:40KW

Dimmensions (Unit: mm)

Main Size of Charger:60KW

- Installation Instruction

  - Before Installation

  - Read all the instructions before using and installing this product.

  - Do not use this product if power cable or charging cable have any damage.

  - Do not use this product if the enclosure or charging connector are broken or open or if there is damage.

  - Do not put any tool, material, ﬁnger or other body part into the charging connec- tor or EV connector.

Warning: The product should be installed only by a licensed contractor and/or licensed technician in accordance with all building codes, elec- trical codes and safety standards.

Warning: The product should be inspected by a qualiﬁed installer prior to initial use. Under no circumstances will compliance with the infor- mation in this manual relieve user of his /her responsibilities to comply with all applicable codes and safety standards.

  - Power feed must be 3 Phase Wye conﬁguration with TN(-S)/ IT/ TT grounding

systems.

  - In the installation of TN(-S) system: the neutral (N) and the PE of the power dis- tribution are directly connected to the earth. The PE of the charger equipment is directly connected to the PE of power distribution and separate conductor for PE and neutral (N).

  - In the installation of IT system: the neutral of the power distribution system is isolated from the earth. The PE of the charger equipment is isolated to the PE of power distribution to the earth.

  - In the installation of TT system: the neutral (N) and the PE of the power distribu- tion are directly connected to the earth. The PE of the charger equipment is iso- lated to the PE of power distribution to the earth.

  - The capacity of power supply should be higher than 33.0kVA in order to function correctly.

  - The product should be installed in free air area and keep at least 30cm clearance distance to all air vent of the product.

  - Need sufficient space for product installation and maintenance, please keep not less than 60cm clearance distance from all around the product.he product should be installed in free air area and keep at least 30cm clearance distance to all air vent of the product.

  - Grounding and Safety Requirement

  - The product must be connected to a grounded, metal, permanent wiring system. Connections shall comply with all applicable electrical codes.

  - Ensure no power is connected at all times when installing, servicing, or maintain- ing the charger.

  - Use appropriate protection when connecting to main power distribution network.

  - Use appropriate tools for each task.

CAUTION: The disconnect switch for each ungrounded conductor of AC input shall be provided by installation contractor or technician.

CAUTION: A cord extension set or second cable assembly shall not be used in addition to the cable assembly for connection of the EV to the QTEV.

  - Service Wiring

  - Ground Connection

Always connect the Neutral at the service to Earth Ground. If ground is not pro- vided by the electrical service then a grounding stake must be installed nearby. The grounding stake must be connected to the ground bar in the main breaker panel and Neutral connected to Ground at that point.

  - 400Vac(Line to Line) Three-Phase

CAUTION!

This is feed from Wye-connection power grid, the Wall Mount DC Fast Charger can connect to L1, L2 or L3, and Neutral. Earth ground must be connected to neutral at only one point, usually at the breaker panel.

L

230Vac 230Vac

Neutral 400Vac

PE

230Vac

L3 1

L2

400V Three-Phase Wiring Connection

DANGERS

Be Aware of High Voltage!

WARNING!

Earth Connection is Essential!

  - Unpack the charger

WARNING!

Charger weight might >80Kg!

Be careful during unpack process.

Box

Accessories

STEP 2.

Remove the packaging ﬁlm and the paper cover. Accessories (wall mount)

are packed in a carton.

STEP 1.

Remove the surrounding boards

STEP 3.

Remove the surrounding cardboard and film. Take out the Charger and Gun holders.

1

2

- Gun holders

- Charger

|  | User Manual (x1) | φ6 Expansion Pipe (x6) | M4*40 Screw (x6) |
| --- | --- | --- | --- |
| Wallbox(x1) | RFID CARD (x2) | Key (x2) | SD card(x1) |

  - Recommended Tools for Installation and Inspection

    - Recommended Tools for Installation

| Type | Description |
| --- | --- |
| Philips Screwdriver | No. 2 and 3 |
| Shifting Wrench | 8" (24mm) |
| Ball-Head Hex Key | 2.5mm and 5mm |
| Socket Screwdriver | No. 8 ,10 and 17 |
| Electrical Tape | Black / 15mm Width |
| AC Input Cable of 30KW | 16mm2 Cable x 5 (L1,L2,L3,N,PE) |
| AC Input Cable of 40KW | 25mm2 Cable x 5 (L1,L2,L3,N,PE) |
| AC Input Cable of 60KW | 35mm2 Cable x 5 (L1,L2,L3,N,PE) |
| Crimping Pliers for Ring Terminal | Applied for 16- 25mm2 |
| Machine Drill |  |
| Wire Cutters |  |
| Level Ruler |  |

    - Recommended Tools for Inspection & Commissioning

| Type | Description |
| --- | --- |
| EV or EV Simulator | Meet CCS2 standard |
| Multiple Meter | 1000V |
| Current Probe | 100Amp |
| RFID Authorized Card |  |
| RFID No Valid Card |  |
| Door Key |  |
| Needle-Nose Plier |  |
| Laptop or PC & CAT6 cable | For Charger Conﬁguration |

  - Installation Procedure

Taking 30KW as an example

STEP 1.

Place the wall-mounted bracket between 600mm (24 inches) and 1.2m (4 feet) above the floor, and then attach 4 pcs 3/8”expansion screws to the wall-mounted bracket. (Unit: mm)

Unit: mm

STEP 2.

Install the four tenons on the rear side of the charger into the grooves on the wall-mounted bracket.

STEP 3.

Screw 2 sets M6 screws to the bottom of the charger to ﬁx the charger on the

bracket.

STEP 4.

Keep the hook-shape holders as cable holder or disassemble them if not necessary.

STEP 5.            30KW

Please use XLPE power cables or equivalent for AC input connection, power cable outer diameter is between 32 and 40mm. Each wire shall be crimped with the corresponding terminal before feeding.  And then feeding the cable from bottom side and passing through the cable gland. L1, L2, L3, N, and PE are connected to the docking terminals as shown in the figure below.

Installing the AC Input Connect

STEP 6.           40KW

Please use XLPE power cables or equivalent for AC input connection, power cable outer diameter is between 32 and 40mm. Each wire shall be crimped with the corresponding terminal before feeding.  And then feeding the cable from bottom side and passing through the cable gland. L1, L2, L3, N, and PE are connected to the docking terminals as shown in the figure below.

STEP 7.           60KW

Please use XLPE power cables or equivalent for AC input connection, power cable outer diameter is between 32 and 40mm. Each wire shall be crimped with the corresponding terminal before feeding.  And then feeding the cable from bottom side and passing through the cable gland. L1, L2, L3, N, and PE are connected to the docking terminals as shown in the figure below.

  - Installation Inspection & Commissioning

    - Environmental Check

| Item | Status | Remark |
| --- | --- | --- |
| Ambient Temperature |  |  |
| Ambient Humidity |  |  |
| Sunshade |  | Recommended but not required. |
| Rain Canopy |  | Recommended but not required. |
| Air Circulation / Drafty |  |  |
| Dust Level |  |  |
| Anti-Vandalism Measures |  |  |

    - External Infrastructure Readiness & Check

| Item | Status | Remark |
| --- | --- | --- |
| Input Wirings & Terminals |  | Type/ Length/ Cross Section |
| Key & Lock of Cabinet Door |  |  |
| Fixing Screws |  | Type / No |
| No Fuse Breaker (NFB) |  | Notice: Current rating of NFB shall be higher than 63 Amp |
| Residual Current Device (RCD) |  | Notice: Maximum RCD residual current shall not excess 30mA |
| Input Electricity Capacity |  |  |
| Input Electricity Conﬁguration |  | Wye |
| Grounding Resistance |  | <50Ω |
| Grounding System |  |  |
| Input Voltage & Frequency |  |  |
| Network Connection & Quality |  | LAN/ Wi-Fi/4G |

    - QTEV Check – Static (Non-Powered)

| Item | Status | Remark |
| --- | --- | --- |
| Outlook |  |  |
| Labeling & Warning Signs |  |  |
| Package (Accessory) List |  |  |
| Robustness of Input Wirings |  |  |

    - QTEV Check - Power On

| Item | Status | Remark |
| --- | --- | --- |
| Screen On |  |  |
| Acoustic Noise |  |  |
| Screen Display & Function |  |  |
| Time Display Correctly |  |  |
| Network Connection Quality |  |  |
| Cooling Fans Operation & Noise |  |  |
| Led Status Indication |  |  |
| QTEV Setting |  |  |
| Function of Engineer Mode |  |  |
| Version of H.W. & F.W. |  |  |
| Remote Control & Monitoring |  |  |
| Backend Server Connection |  |  |

    - QTEV Check - Charging

| Item | Status | Remark |
| --- | --- | --- |
| User Authorization –RFID |  |  |
| User Authorization –QR Code |  |  |
| User Authorization –Others. |  |  |
| Waiting Time of Connection Check |  |  |
| Reading of Each Display Item |  |  |
| Full Charge Test |  |  |
| Function of Electronic Lock |  |  |
| Reading of Engineer Mode |  |  |
| Airflow & Noise of Cooling Fan |  |  |
| Charging Record ( log ) Upload |  |  |
| Remote Control & Monitoring |  |  |

    - QTEV Check –System Power Button

| Item | Status | Remark |
| --- | --- | --- |
| Emergency Stop Button |  |  |

- Network Setting

  - Wi-Fi Network Setting

Laptop with RJ45 interface.

Connect RJ45 cable from Laptop to charger’s RJ45 port.

Setup parameters in the Webservice.

Step 1.

Open web service browser, type the IP address of charger“192.168.2.5:8080” into the URL bar to access the web

page of charger.

Password: 12345678

Step 2.

Select Wi-Fi Module

Select Wi-Fi modes and ﬁll in SSID and Password according to your application, if not required, just keep default.

- Operation Process

  - RGB LED indicators

| Charger status | LED performance |
| --- | --- |
| Standby | green blink |
| plug in | yellow |
| swipe/punch a card | yellow |
| charging | Light green breath |
| Fault status | Red flashing |

  - LCD indicators

the EMN series config a 7-inch LCD screen, which is mainly used to display various status information of the charging station.

- Icons or instructions in each display area

Fig. 1-2 Display of icons and instructions

In Fig. 1-2, there are three areas to display icons or instructions, with the specific meanings as follows:

| No. | Icon |  | Description |  |
| --- | --- | --- | --- | --- |
| Area ① |  |  |  |  |
| 1 |  |  | Connected a network through 4G cellular |  |
| 2 |  |  | Connected a network through WIFI |  |
| 3 |  |  | Connected a network through Ethernet |  |
| Area ② |  |  |  |  |
| 4 | Version |  | Software version |  |
| 5 | SN |  | Serial number of QTEV |  |
| Area ③ |  |  |  |  |
| 5 | status |  | QTEV status information |  |
| Area 4 |  |  |  |  |
| 6 |  | Settings |  | Set charging station parameters |

- As shown in Fig. 1-3,1-4,1-5,1-6, the LCD screen displays 4 types picture in normal state.

Fig. 6-3 Display of Preparing

Fig. 6-4 Display of Charging

Fig. 6-5 Display of Finished

- Click the settings icon three times to enter the settings interface, the picture displayed on the LCD screen is shown in Fig. 6-6.

- Enter password: 1234

Fig. 6-6 Display of  Management

- If the charging process fails or the equipment fails, the picture displayed

on the LCD screen is shown in Fig. 6-7.

Fig. 6-7Display of fault state

  - Troubleshooting

- Please follow the instruction in the table when errors occur during the charging process.

- Or please contact the DC Quick Charger provider for further instructions.

- If an emergency occurs push the Emergency Stop Button to stop charging imme- diately.

  - Status Codes

*For latest status code, please visit our website.

| Status Code | Description | Solution |
| --- | --- | --- |
| 0001 | Emergency stop | If no fault occurs,please rotate the button clockwise to reset the charger. |
| 0002 | CCS output fuse blew | If fault occurs,please check&replace the fuse. |
| 0003 | AC input contactor 1 welding | If fault occurs,please check&replace the contactor. |
| 0004 | CCS output relay welding | If fault occurs,please check&replace the Relay. |
| 0005 | CCS connector temperature sensor broken | If fault occurs,please check&replace the sensor. |
| 0006 | Relay control module /smart box broken | If fault occurs,please check&replace the Relay control module. |
| 0007 | CCS Power module fault | If fault occurs,please replace the CCS Power module. |
| 0008 | Maximum Output Current setup error | If fault occurs,please reset the correct value. |
| 0009 | Maximum Output Voltage setup error | If fault occurs,please reset the correct value. |
| 0010 | BLE module broken | If fault occurs,please replace the BLE module. |
| 0011 | 4G module broken | If fault occurs,please replace the 4G module. |
| 0012 | Ethernet BLE module broken | If fault occurs,please replace the Ethernet BLE. |
| 0013 | wifi module broken | If fault occurs,please replace the wifi module. |
| 0014 | CCS connector OTP | If fault occurs,please check&reset the OTP value. |
| 0015 | SPD trip | If fault occurs,please replace the SPD Module. |
| 0016 | CCS ground fault detection timeout (GFD) | If fault occurs,please check the Ground line. |
| 0017 | RFID module communication fail | If fault occurs,please check Communication line with RFID. |
| 0018 | Power module communication fail | If fault occurs,please check can line with power module. |
| 0019 | Door open | If fault occurs,please closed the door &recharge with vehicle. |
| 0020 | System fan decay | If fault occurs,please replace the fan. |
| 0021 | AC Ground Fault | If fault occurs,please check the Ground line. |
| 0022 | CCS EV communication Fail | If fault occurs,please check Connecting wire with vehicle. |

- Maintenance

  - General Maintenance

- The DC Fast Charger is cooled by forced air. Please keep charger in a ventilated location and do not block the air vents of the DC Fast Charger .

- Please clean or replace the air filters regularly to ensure the DC Fast Charger works properly.

- Clean the DC fast Charger at least three times a year, keep the exterior clean at all times.

- Clean the outside of the cabinet with damp cloth or wet cotton towel, only use low-pressure tap water and cleaning agents with PH level between 6 to 8.

- Do not apply high-pressure water jets.

- Do not use cleaning agents with abrasive components and do not use abrasive tools. Improper cleaning agents might spoiled coating, painting, surface, bright- ness and durability of all exterior parts.

- If there is water intruding into the DC Fast Charger then please cut off the power source immediately and contact the DC Fast Charger provider for repair.

- Please make sure the charging connector is returned to the holder of the charging connector after charging to prevent damage.

- If there is damage to the charging connector, charging cable or holder of the charging connector then please contact the DC Fast Charger provider.

- When using the DC Fast Charger please handle properly. Do not strike or scrape the cabinet or touch screen.

- If the enclosure or touch screen is broken, cracked, open or shows any other indi- cation of damage then please contact the Standalone DC Fast Charger provider.

WARNING: Danger of electrical shock or injury. Turn OFF power at the panelboard or load center before working on the equipment or remov- ing any component. Do not remove circuit protective devices or any other component until the power is turned OFF.

- Disconnect electrical power to the DC Fast Charger before any maintenance work to ensure it is separated from the supply of AC mains. Failure to do so may cause physical injury or damage to the electrical system and charging unit.

Note:

- Before switching off main breaker to begin maintenance, please record the status code number on the LCD monitor.

- After switching off the key switch the circuit before the main terminal is still hazardous. Only visual inspection can be operated.

- Maintenance of the DC Fast Charger shall be conducted only by a qualified technician.

- After opening the front door of the DC Fast Charger, turn off the main breaker and auxiliary breaker before any maintenance work.

- Replace the ventilation ﬁlter every six to twelve months.

Limited Product Warranty

The warranty period for this charger is two years.

Any spare parts provided by YINGLI Technology and used as replacements for re-

pair are covered by a ﬁve-year guarantee.

Replacement and repair parts manufactured by alternative manufacturers to those on the maintenance parts are only allowed if authorized by YINGLI.

Warranty Exclusions:

- Damage or rendered non-functional as a result of power surges, lighting,

earthquake, ﬁre

- flood, pest damage, abuse, accident, misuse, negligence or failure to maintain the product or other event beyond YINGLI’s reasonable control or not arising from normal operating condition.

- Cosmetic or superﬁcial defect, dents, marks or scratches after use.

- Components which are separate from the product, ancillary equipment and consumables, such as door key, RFID card, air ﬁlter, fuse, cable, wires and con- nectors.

- Damage as a result of modiﬁcations, alterations or disassembling which were

not pre-authorized in writing by YINGLI.

- Damage due to the failure to observe the applicable safety regulations govern- ing the proper use of the product.

- Installed or operated not in strict conformance with the documentation, in- cluding without limitation, not ensuring sufﬁcient ventilation for the product as described in YINGLI installation instruction.

If a defect in the product arises and valid claim is received within the warranty pe- riod, your sole and exclusive remedy will be for YINGLI, at its sole discretion and to extent permitted by law, to

- Repair the defect in the product at no charge, using new or refurbished parts.

- Exchange the product with new or refurbished product that is functionally equivalent to the original product.

Any remedy hardware product will be warranted for the remainder of the original warranty period or 90 days from delivery to the customer, whichever is longer.

In order to receive the remedy set for above, you must contact YINGLI during the warranty period and provide the model number, series number, proof of purchase, and date of purchase

Appendix - Package list

| Item | Description | Quantity | Remark |
| --- | --- | --- | --- |
| 1 | QTEV | 1 |  |
| 2 | User Manual | 1 |  |
| 3 | OQC Report | 1 |  |
| 4 | RFID Card | 2 |  |
| 5 | Key of Cabinet | 2 |  |
| 6 | Wall-Mounted Bracket | 1 |  |
| 7 | Gun Holder | - | Single Gun*1pcs, Dual Gun*2pcs Refer to Chapter 2.2 Table |
| 8 | 5/16” Expansion Screw | 4 | Each Gun Holder*2pcs |
| 9 | 3/8” Expansion Screw | 4 | Wall-Mounted Bracket*4pcs |
| 10 | M6 Screw | 2 | Wall-Mounted Bracket*2pcs |
| 11 | 2.5mm Ball-Head Hex Key | 1 |  |